Guide to Drafting a Specification for

High Capacity Drilled and Grouted Micropiles

for Structural Support

This document was prepared by the Deep Foundations Institute (DFI) Micropile Committee from 1996 to 2001 and endorsed by the ADSC-IAFD Micropile in October 2001.   If you have received this document from a source other than purchase from DFI or ADSC, please contact DFI at (201) 567-4232 to officially purchase at a modest price and support the future foundation developments of DFI.

Foreword

The three types of specifications which are used for micropile work are:

- Performance Specifications: The contractor is permitted control over certain design and/or construction procedures but must demonstrate to the owner through testing and/or certification that the final product meets the specified performance criteria.  This method allows and encourages the contractor to provide a competitive and/or innovative micropile design within the framework of the overall design requirements.  The responsibilities for the work are shared between the owner and the contractor.

- Open Specifications: These leave the scope and design of the installation up to the micropile contractor.  This method is the most common for securing bids on temporary micropile work.  The responsibility for design and performance is clearly placed on the contractor.  Open specifications are not recommended for permanent applications.  This method allows the contractor to select the most economical micropile system.

- Prescriptive Specification: The Owner describes specific procedures that must be followed, but which may not necessarily describe the objective of the work.  When prescriptive specifications are used, the owner is responsible for the proper performance of the system.  The contractor is responsible for satisfying the details of the specifications.

Performance specifications are the most common and best reflect the challenges and interests of micropile technology and applications.

The owner, designer and contractor will together be responsible for the tasks associated with the design, installation, acceptance, and performance of the micropiles.  The installation of micropiles requires specialized equipment, techniques, and appropriate workmanship.  Not every detail of the work can be specified, and not every potential problem can be anticipated.  Therefore, a contractor who has demonstrated experience in micropiles must be selected to execute the work required.

A list of the major tasks to be performed on a micropile project is shown in Table 1 of the Model Specifications.  The owner must select the type of specification and procurement system.  The responsible party for each task must be clearly identified and mutually agreed upon at the earliest point in the contracting process.  The completed Table 1 must be included in the specification and/or drawings.

The process of continuous communication between all the parties involved, regardless of the allocation of responsibilities and tasks, is essential to achieve a quality result.  In particular, clear communication and close cooperation are important in the start up phase.  In addition, a timely preparation and review of all submittals is critical.

This model specification can be adapted to each of the three types of specifications, although, reflecting the most common circumstances, it is primarily written for the “performance” mode.  The identity of the “contractor” and the “owner” is always well defined, unlike that of the “engineer”.  For example, “the engineer” may be, under different types of contract, either the contractor or the owner, or employed by either.  It is most common however, to find that the engineer, even in Prescriptive or Open specifications, is a third party agency, employed by the owner to serve the owner’s best interests during the various stages of the contract.

For the purposes of this Model Specification, the subject is a high capacity micropile (with working loads of 25 tons minimum), comprising a steel reinforcement grouted into a pre-drilled hole.  The steel is intended to accept most of the applied load.  The piles will be typically 4 to 12 inches in diameter and will accept load directly (FHWA Case 1 elements, Figure 1) axially and/or laterally, to provide structural support.  Groups or networks (FHWA Case 2) of micropiles as used for slope stabilization, ground improvement or support of excavation (Figure 1) are not addressed herein, although much of this Specification would equally apply.

It is essential that the drafter of the specification accurately and completely modifies this model to suit his particular case.

In the following document, sections that may be regarded as “Commentary” as opposed to “Specification” are denoted in italic type, thus.

Reflecting current practice, the document is presented in Imperial Units.  A table of conversions is attached.

The following is a list of general references which will provide additional background to micropile technology:

“Drilled and Grouted Micropiles:  State of Practice Review, Volumes I, II, III, AND IV.”  Prepared for the Federal Highway Administration by D.A. Bruce and I. Juran, Publication Nos. FHWA-RD-96-016. –017, -018, AND –019, July 1997.

“International Workshop on Micropiles.” (1997) Proceedings of Specialty Conference on Micropiles, Seattle, WA, September 26-28, 463 p.  Organized by DFI (D.A. Bruce , Bruce, and M.E. Caves)

Ground Improvement, Reinforcement, and Treatment:  Developments 1987-1997,  Chapter 26 on Micropiles, Proc. of Sessions Sponsored by the Committee on Soil Improvement and Geosynthetics of the Geo-Institute of the American Society of Civil Engineers, Logan, UT, July 17-19, Ed. by V.R. Schaefer, Geotechnical Special Publication No. 69, pp. 151-175.

“International Workshop on Micropiles” (1999) Proc. of Second Workshop on Micropiles, Ube, Japan, October 4-7.  Organized by the Yamaguchi University (F. Miura)

“International Workshop on Micropiles” (2000) Proc. of Third Workshop on Micropiles, Türkü, Finland, June 5-7.  Organized by Tampere University of Technology (J. Lehtonen)

“Micropile Design and Construction Guidelines”. (2000)  Prepared by D.B. Murphy Co. for FHWA.  Publication No. FHWA-SA-97-070.

Figure 1. CASE 1 and CASE 2 micropiles (fundamental classification based on supposed interaction with the soil) (FHWA, 1996).

Figure 2. Table of conversions.

model specification

1.	general

1.1	Purpose of Specification

This specification, along with the drawings, encompasses the furnishing of all designs, materials, products, accessories, tools, equipment, services, transportation, labor and supervision, and installation techniques required for testing and installing of micropiles and pile-top attachments.

This specification may require modification by the specification writer to accommodate unusual and/or unforeseen site and subsurface conditions and the particular circumstances of the project.  Care must be taken to avoid any internal inconsistencies.

1.2	Scope of the Work

The work consists of furnishing all necessary engineering and design services (if required), supervision, labor, materials, and equipment to perform all work necessary to install and test the micropiles, at (location, City, State, Subdivision) for (Company, State or Private Authority) per the specifications described herein, and as shown on the design drawings. The micropile contractor shall install a micropile system that will develop the load capacities indicated on the drawings.  The micropile load capacities and measurements may be verified by testing if required and as specified herein.  The responsibilities and duties of the respective parties for this project are summarized in Table 1.

Table 1.  Tasks and responsibilities to be allocated for micropile works.

| TASK | RESPONSIBLE PARTY* |
| --- | --- |
| 1 | Site investigation, geotechnical investigation, site survey, and potential work restrictions. |  |
| 2 | Decision to use a micropile system, requirement for a pre-contract testing program, type of specification, and procurement method and levels of prequalification. |  |
| 3 | Obtaining easements. |  |
| 4 | Overall scope of work, design of the piled structure, and definition and qualification of safety factors. |  |
| 5 | Structure Loads (Vertical , horizontal, etc.) |  |
| 6 | Calculation/estimation of tolerable total structural movement in service. |  |
| 7 | Definition of service life (temporary or permanent) and required degree of corrosion protection. |  |
| 8 | Type and number of tests (pre-contract and production) |  |
| 9 | Micropile locations, spacing and orientation, and pile load. |  |
| 10 | Minimum total pile length, depth to bearing stratum. |  |
| 11 | Micropile components and details. |  |
| 12 | Determination of load transfer length or depth of rock socket |  |
| 13 | Details of corrosion protection. |  |
| 14 | Details of pile connection to structure (e.g., for static and seismic conditions. |  |
| 15 | Record keeping and preparation of Drawings. |  |
| 16 | Evaluation of test results. |  |
| 17 | Construction methods, schedule, sequencing, and coordination of work. |  |
| 18 | Requirements of QA/QC program. |  |
| 19 | Supervision of work. |  |
| 20 | Maintenance and long-term monitoring. |  |

*To be filled in by specification writer.

1.3	Qualifications of the Contractor

The micropile contractor shall be fully experienced in all aspects of micropile design and construction, and shall furnish all necessary plant, materials, skilled labor, and supervision to carry out the contract.  The contractor will have successfully completed at least five projects in the previous five years of similar scope and size.  He must also provide resumés of key personnel who will be present on site (and will be materially involved) and who will each have at least three years of relevant experience.  These personnel include superintendent, driller, and project engineer/manager.  Alternatively, the owner can provide a list of prequalified micropile contractors.

The micropile contractor shall not sublet the whole or any part of the contract without the express permission in writing of the Owner.

1.4	Related Project Specifications

To be determined by the specification writer.

1.5	Definitions

A partial list follows.  The Owner may wish to add other specific, project-related items.

Admixture:	Substance added to the grout to either control bleed and/or shrinkage, improve flowability, reduce water content, retard setting time, or resist washout.

Alignment Load (AL):	A nominal load applied to a micropile during testing to keep the testing equipment correctly positioned.

Apparent Free Micropile Length:	The length of pile which is apparently not bonded to the surrounding ground, as calculated from the elastic load extension data during testing.

Bond Breaker: 	A sleeve or coating placed over the steel reinforcement to prevent load transfer.

Bonded Length:	The length of the micropile that is bonded to the ground and which is conceptually used to transfer the applied axial loads to the surrounding soil or rock.  Also known as the load transfer length.

CASE 1 Micropile:	A pile designed to accept load (either axial or lateral) directly, and transfer it to an appropriate bearing stratum.  Usually comprises significant steel reinforcement.

CASE 2 Micropile:	One of a network of low capacity piles used to delineate and internally reinforce a volume of composite, reinforced pile/soil material.

Casing:	Steel pipe introduced during the drilling process to temporarily stabilize the drill hole. Depending on the details of the micropile construction and composition, this casing may be fully extracted during or after grouting, or may remain partially or completely in place, as part of the final pile configuration.

Centralizer:	A device to centrally locate the reinforcing element(s) within the borehole.

Contractor:	The person/firm responsible for performing the micropile work.

Core Steel:	Reinforcing bars or pipes used to strengthen or stiffen the pile, excluding any left-in drill casing.

Corrosion Inhibiting Compound:	Material used to protect against corrosion (and/or lubricate the reinforcing steel inside a bond breaker).

Coupler:	The means by which the load can be transmitted from one partial length of reinforcement to another.

Creep Movement:	The movement that occurs during the creep test of a micropile under a constant load.

Design Load (DL):	Anticipated final maximum service load in the micropile.

Duplex Drilling:	A drilling system involving the simultaneous advancement of (inner) drill rod and (outer) drill casing.  Flush from the inner drill rod is permitted to exit the borehole via the annulus between rod and casing.

Elastic Movement:	The recoverable movement measured during a micropile test.

Encapsulation	A corrugated tube protecting the reinforcing steel against corrosion.

Free (unbonded) length:	The designed length of the micropile that is not bonded to the surrounding ground or grout during testing.

Micropile:	A small diameter, bored, cast-in-place pile, in which most of the applied load is resisted by the steel reinforcement.

Overburden:	Non-lithified material, natural or placed, which normally requires cased drilling methods to provided an open borehole to underlying strata.

Post Grouting:	The injection of additional grout into the load transfer length of a micropile after the Primary grout has set.  Also known as regrouting or secondary grouting.

Preloading:	The principle whereby load is applied to the micropile, prior to the micropile's connection to the structure, to minimize any structural movement in service.

Primary Grout:	Portland cement based grout that is injected into the micropile hole prior to or after the installation of the reinforcement to provide the load transfer to the surrounding ground along the micropile and affords a degree of corrosion protection in compression.

Proof Test:	Incremental loading of a micropile, recording the total movement at each increment.

Reinforcement:	The steel component of the micropile which accepts and/or resists applied loadings.

Residual Movement:	The non-elastic (non-recoverable) movement of a micropile measured during load testing.

Safety Factor:	The ratio of the ultimate capacity to the working load used for the design of any component or interface.

Single Tube Drilling:	The advancement of a steel casing through overburden usually aided by water flushing through the casing.  Also known as “external flush.”  The fluid may or may not return to the surface around the casing, depending largely on the permeability of the overburden.

Test Load (TL):	The maximum load to which the micropile is subjected during testing.

Tremie Grouting:	The placing of grout in a borehole via a grout pipe introduced to the bottom of the hole.  During grouting, the exit of the pipe is kept at least 10 feet below the level of the grout in the hole.

Type A-D:	Classification of micropiles based on method and pressure of grouting (see FHWA, 1997).

Working Load:	Equivalent term for Design Load.

1.6	Allowable Tolerances

The tolerances quoted in this section are maxima.  Depending on the structural implications, the actual values set on a particular project may have to be lower.

1.6.1	Centerline of piling shall not be more than 3 in. from indicated plan location.

1.6.2	Pile-hole alignment shall be within 2% of design alignment.

1.6.3	Top elevation of pile shall be within +1 in. to –2 in. of the design vertical elevation.

1.6.4	Centerline of core reinforcement shall not be more than ¾ in. from centerline of piling.

1.7	Design Criteria

1.7.1	The micropiles shall be designed to meet the specified loading and movement conditions as shown on the drawings.  The calculations and drawings required from the Contractor shall be submitted to the Owner for review and acceptance in accordance to Section 3.1 “Pre-construction Submittals”.

1.7.2	The allowable working load on the pile shall not exceed the following values:

1.7.2.1	For compression loads:

Pallc = (0.33 * fc * Agrout + 0.4 * fycasing * Acasing + 0.4 * fybar * Abar)

where:		Pallc 	=	allowable working load (compression)

fc	=	Unconfined Compressive Strength of grout

Agrout	=	area of grout

fycasing	=	yield strength of casing up to 80 ksi

Acasing	=	area of steel casing (with allowance for corrosion if appropriate)

fybar 	=	yield strength of rebar/core steel up to 80 ksi

Abar	=	area of rebar/core steel

The maximum useable strength of the steel of 80 ksi is based on the typical ultimate concrete strain of 0.003 (29000 ksi * 0.003 = 87 ksi).  80 ksi is also the maximum steel strength used in ACI 318.  In the cased section, additional confinement of the casing yields higher grout strength due to triaxial effects.

These allowable stresses may be increased if the micropile designer and Contractor are willing to exceed 80% fy during testing or can provide substantiating data of the composite strength. For example, FHWA Implementation Manual (2000) permits, for compression, 0.4* fc  and 0.47* fycasing and core steel.

1.7.2.2	For tension loads:

Pallt = 0.6* (fycasing * AcasingT + fybar * Abar)

where:	Pallt 	=	allowable working load (tension)

fycasing	=	yield strength of casing

AcasingT	=	area of steel casing (at threaded joints if applicable)

fybar	=	yield strength of rebar/core steel

Abar	 =	area of rebar/core steel

Care must be used in evaluating tension on threaded joints of drill casing, however, the  load tests may verify threaded joint tension adequacy. The tension resistance of the casing and joints may also be conservatively neglected in design ( use AcasingT = 0 ).

1.7.3	The ultimate structural capacity shall be determined as:

1.7.3.1	Compression

Puc = (0.85 * fc * Agrout + fycasing * Acasing + fybar * Abar)

where:	Puc	 =	ultimate structural capacity (compression)

fc	=	UCS of grout

Agrout	=	area of grout

fycasing	=	yield strength of casing up to 80 ksi

Acasing 	=	area of steel casing (corroded if appropriate)

fybar	=	yield strength of rebar/ core steel up to 80 ksi

Abar 	=	area of rebar/ core steel

The maximum useable strength of the steel of 80 ksi is based on the typical ultimate concrete strain of 0.003 (29000 ksi * 0.003 = 87 ksi).  80 ksi is also the maximum steel strength used in ACI 318.

1.7.3.2	Tension

Put = fycasing * Acasing + fybar * Abar)

where:		Put 	=	ultimate structural capacity (tension)

fycasing	=	yield strength of casing

Acasing	=	area of steel casing (at threaded joints if applicable)

fybar	=	yield strength of rebar

Abar	=	area of rebar

1.7.4	Lateral Load and Bending: Where lateral loads are indicated on the plans, the bending moment from these lateral loads shall be determined using COM624 or equal.  The soil parameters (c, (, (, and k) for use with COM624, or equal, are provided in the geotechnical reports.  The combined bending and axial load factor of safety of the micropile shall be as determined by the Owner, and, for this project is as follows for each load combination:

1.7.5	The micropile top attachment shall effectively distribute the design load (DL) to the concrete footing, such that the concrete bearing stress does not exceed those in the ACI Building Code and the bending stress in the steel plates does not exceed AISC Allowable stresses for steel members.

1.7.6	The geotechnical capacity shall not be relied upon from the following stratigraphic units ___________.

The overall length of a micropile will be selected such that the required geotechnical capacity is developed by skin friction between grout and ground over a suitable length in an appropriate stratum.

Micropiles founded in rock may conceptually develop their capacity primarily through point bearing and secondarily by skin friction. Care must always be taken to ensure that the pile is not terminated on a boulder, or on rock with very soft material below.  In addition, appropriate and consistent drill refusal criteria must be identified, and verified in the field.

    - Corrosion Protection

The whole of this section is optional (see next paragraph). Therefore the provisions of this section and Section 4-9 below, may not be required in the Specification.  If this section is not used, then Section 4.9 should be deleted as well.

Regarding protection of the steel reinforcement against corrosion, the degree and extent of corrosion protection must be specified by the Owner (Table 1) and are an important design issue.

The degree and extent of corrosion protection is a function of loading condition and corrosive aggressiveness of the ground However, for piles in tension and/or in aggressive ground, the need for corrosion protection must be carefully determined, and the details specified.

Corrosion resistant coatings on permanent drill casing are impractical due to the abrasive action of the soil on the outer surface of the casing and probable resulting damage to or wearing off of the coating.

The following requirements are typical. The specifier should review and edit as appropriate for the specific project:

Corrosion protection requirements for the various elements shall be provided meeting the requirements of Table 2 for:

Loading Type: _________	to be filled in by Specifier with optional location limits defined (e.g. Tension, Compression)

Ground : ___________ Aggressive or Non-Aggressive with optional defined limits of location and Elevation to be filled in by Specifier

For guidance on aggressiveness classification, see Appendix A.

## TABLE 2

| Corrosion Protection |
| --- |
| Loading | Tension1 | Compression |
| Ground | Aggressive2 | Non aggressive | Aggressive2 | Non-aggressive |
| Casing | Do not rely on casing for load capacity, | None provided tension load on casing is less than 20% of casing thread strength OR Do not rely on casing for load capacity | Min 01/16” corrosion loss on outside The Specifier may desire to use a different corrosion loss per Appendix B. | None The Specifier may desire to use a corrosion loss per Appendix B. |
| Coresteel | epoxy coating3 OR galvanization3 OR encapsulation in plastic sheath3 AND Grout cover4 | bare steel5 OR epoxy coating3 OR galvanization3 OR encapsulation in plastic sheath3 AND Grout cover4 | a. Grout Cover4 AND The Specifier may desire to add other options listed for tension. | a. Grout Cover4 |

NOTES:

Lettered items are options.

For guidance on aggressiveness classification, see Appendix A.

- Sustained tension or temporary tension ( wind, seismic, impact) on life critical structural.  For temporary tension on normal structures, corrosion protection under Compression is often used.

- Corrosion protection must extend 15 feet below corrosive material

- Coresteel corrosion protection must extend a minimum 5 feet into casing

- Minimum 1 inch in soil and 0.5 inch in rock.  If protective coatings (epoxy, galvanization, or encapsulation) are provided in compression, minimum cover may be 0.25 inches in soil or rock.

- Not recommended for sustained or frequent tension loads

1.8	Ground Conditions

The test borings as shown on the boring location plan and logs of borings as described in the Geotechnical Report are believed to be representative of the conditions likely to be encountered on the site, and are to be used as the basis for micropile design in conjunction with the appropriate levels of engineering judgement and experience.  The sources of data are as follows:

If, during installation of a pile, an obstruction is encountered that prevents the practical advancement of the hole, the hole shall be abandoned and filled with grout.  A new pile shall be drilled at a location to be determined by the Owner, although it must be acknowledged that in certain structures, relocation options may be severely limited, and further attempts at the original location with different methods may be required.

If during drilling, obstructions are encountered of a frequency, composition and location that were not portrayed, inferable, expected and/or notified at the time of preparation of the bid, the additional costs utilized in trying to overcome such obstructions shall be paid for.

All available information on the ground and site conditions must be made available to all bidders at the time of bid preparation and should be regarded as a part of the subsequent contract documents.  It is not reasonable to expect bidders to conduct supplemental site investigations prior to bidding, at their own risk and cost, unless the specific contract requirements call for it (Table 1) and provide for appropriate remuneration.  It is in the best interests of all parties that a mandatory site visit and pre-bid meeting is held so that the details of the project and the specifications can be thoroughly discussed.  All these steps will help avoid technical and contractual problems developing during the execution of the works, and will help all parties manage their respective risk.

2.	REFERENCED CODES AND STANDARDS

The following publications form a part of this specification to the extent indicated by the specific citations in other paragraphs of this Specification.  In case of conflict, the particular requirements of this specification shall prevail.  The latest publication as of the issue of this specification shall govern, unless indicated otherwise.

2.1	American Society for Testing and Materials (ASTM)

American Association of State Highway and Transportation Officials (AASHTO)

| ASTM | AASHTO | Specification |
| --- | --- | --- |
| A36 | M183, M223 | Structural Steel |
| A82 | M55 | Cold-Drawn Steel Wire for Concrete Reinforcement |
| A252 | --- | Welded and Seamless Steel Pipe Piles |
| A615 | M31 | Deformed and Plain Billet Steel Bars for Concrete Reinforcement |
| A722 | M275 | Uncoated High-Strength Steel Bar for Prestressing Concrete |
| A775 | M282 | Electrostatic Epoxy Coating |
| C33 | M80 | Concrete Aggregates |
| C109 | T106 | Compressive Strength of Hydraulic Cement Mortar |
| C188 | T133 | Density of Hydraulic Cement |
| D3966 | --- | Standard Test Method for Piles Under Lateral Load |
| D1784 | --- | Polyvinyl Chloride (PVC) Pipe (Class 13464-B) |
| C144 | M45 | Aggregates for Masonry Mortar |
| C150 | M85 | Portland Cement |
| C494 | M194 | Chemical Admixtures for Concrete |
| D1143 | --- | Method of Testing Piles Under Static Axial Compressive Load |
| D3350 | M252 | Polyethylene Corrugated Tubing |
| D3689 | --- | Method of Testing Individual Piles Under Static Axial Tensile Load |
| --- | T26 | Quality of Water to be Used in Concrete |

2.2	American Welding Society (AWS):

| D 1.1 | Structural Welding Code – Steel |
| --- | --- |
| D 1.2 | Structural Welding Code – Reinforcing Steel |

2.3	American Petroleum Institute (API)

| 5CT (N80) | Specification for casing and tubing |
| --- | --- |
| RP 138-1 | Recommended Practice – Standard Procedure for Field Testing Water Based Drilling Fluids |

2.4	American Society of Civil Engineers

| ASCE 20-96 | Standard Guidelines for the Design and Installation of Pile Foundations. |
| --- | --- |

2.5	Post Tensioning Institute (PTI)

“Recommendations for Prestressed Rock and Soil Anchors.” (1996).

3.	SUBMITTALS

3.1	Construction Submittals

3.1.1	The Contractor shall prepare and submit to the Owner, for review and approval, working drawings and relevant structural design calculations for the micropile system or systems intended for use at least 21 calendar days prior to planned start of construction (but note also Paragraph 3.1.9).  All design submittals shall be sealed by a Registered Professional Engineer, currently licensed in the State of ____.

3.1.2	The Contractor shall submit a detailed description of the construction procedures proposed for use to the Owner for review.  This shall include a schedule of major equipment resources.

3.1.3	The Working Drawings shall include micropile installation details giving:

3.1.3.1	Micropile number, location and pattern

3.1.3.2	Micropile design load

3.1.3.3	Type and size of reinforcing steel

3.1.3.4	Minimum total bond length

3.1.3.5	Total micropile length

3.1.3.6	Grouting volumes and maximum pressures

3.1.3.7	Micropile top attachment

3.1.3.8	Micropile cut-off elevation

3.1.4	The Contractor shall submit shop drawings for all structural steel, including the micropile components, corrosion protection system, pile top attachment and bond length details to the Owner for review and approval.

3.1.5	The Contractor shall submit certified mill test reports, properly marked, for the reinforcing steel, as the materials are delivered, to the Owner for record purposes.  The ultimate strength, yield strength, elongation, and material properties composition shall be included.  For steel pipe used as permanent casing, or core steel, the Contractor shall submit a minimum of two representative coupon tests or mill certifications (if available) on each load delivered to the project.

3.1.6	The Contractor shall submit the grout mix designs, including details of all materials to be incorporated, and the procedure for mixing and placing the grout to the Owner for approval.  This submittal shall include certified test results verifying the acceptability of the proposed mix designs.

3.1.7	The Contractor shall submit detailed plans for the method proposed for testing the micropiles to the Owner for review and acceptance prior to beginning load tests.  This shall include all necessary drawings and details to clearly describe the test method and equipment proposed.

3.1.8	The Contractor shall submit to the Owner calibration reports for each test jack, pressure gauge, and master pressure gauge to be used.  The calibration tests shall have been performed by an independent testing laboratory and tests shall have been performed within one year of the date submitted. Testing shall not commence until the Owner has approved the jack, pressure gauge and master pressure gauge calculations.

3.1.9	Work shall not begin until the appropriate submittals have been received, reviewed, and approved in writing by the Owner.  The Contractor shall allow the Owner up to 2 weeks to review, comment upon and return the Working Drawing submittal package after a complete set has been received.  Note that any additional time required due to incomplete or unacceptable submittals shall not be cause for delay or impact claims.  All costs associated with incomplete or unacceptable submittals shall be the responsibility of the Contractor (or as otherwise allocated in Table 1).

3.2	Installation Records

The following records will be prepared for the Owner in accordance with the specified division of responsibilities as noted in Table 1.  The records shall be completed within 24 hours after each pile installation is completed.  The records shall include the following minimum information:

3.2.1	Pile drilling duration and observations (e.g., flush return)

3.2.2	Information on soil and rock encountered, including description of strata, water, etc.

3.2.3	Approximate final tip elevation

3.2.4	Cut-off elevation

3.2.5	Rated load capacities

3.2.6	Description of unusual installation behavior, conditions

3.2.7	Any deviations from the intended parameters

3.2.8	Grout pressures attained, where applicable

3.2.9	Grout quantities pumped

3.2.10	Pile materials and dimensions

3.2.11	Micropile test records, analysis, and details

In addition, as-built drawings showing the location of the piles, their depth and inclination, and details of their composition shall be submitted within ________ calendar days of the project completion.

4.	PRODUCTS AND MATERIALS

4.1	Water

Water for mixing grout shall be potable, clean and free from substances which may be in any way deleterious to grout or steel.  If water is not potable, it shall be tested in accordance with AASHTO T26 for acceptability.

4.2	Admixtures

Admixtures shall conform to the requirements of ASTM C494 (AASHTO M194).  Admixtures which control bleed, improve flowability, reduce water content, and retard set may be used in the grout subject to the review and acceptance of the Owner.  Expansive admixtures shall only be added to the grout used for filling sealed encapsulations.  Accelerators will not be permitted.  Admixtures shall be compatible with the grout and mixed in accordance with the manufacturer’s recommendations.  Their use will only be permitted after appropriate field tests on fluid and set grout properties.  Admixtures with chlorides shall not be permitted.

4.3	Cement

All cement shall be Portland cement conforming to ASTM C150 (AASHTO M85) Type I, Type II, or Type III, and shall be the product of one manufacturer.  If the brand or type of cement is changed during a project, additional grout mix tests shall be conducted to ensure consistency of quality and performance in situ.

4.4	Fillers

Inert fillers such as sand may be used in the grout in special situations (e.g., presence of large voids in the ground, when grout take and travel are to be limited) as approved by the Owner.

4.5	Bar Reinforcement

4.5.1	Reinforcing steel shall be deformed bars in accordance with ASTM A615 (AASHTO M31) Grade 60 or Grade 75 or ASTM A722 (AASHTO M275) Grade 150.

4.5.2	For cases of tensile loading, bar couplers, if required, shall develop the ultimate tensile stress of the bar, without any evidence of failure.  For compressive loading, the coupler shall be compatible with efficient load transfer and overall reinforcement performance requirements.

4.6	Pipe/Casing

If the casing is to be relied upon to carry loads or reduce deflection, the permanent steel casing/pipe:

1.	Shall meet the tensile requirements of ASTM A252, Grade 3, except the minimum yield strength shall be as used in the design submittal (typically 50,000 psi to 80,000 psi) and minimum elongation shall be 15%.

2.	May be new “Structural Grade” (a.k.a. “Mill Secondary”) steel pipe meeting above but without Mill Certification, free from defects (dents, cracks, tears) and with two coupon tests per truckload.

It is recommended that if welding of the high strength steel casing is required, the Owner will require the submittal of a welding procedure, prepared by a welding specialist, for review prior to any welding operation.

4.7	Plates and Shapes

Structural steel plates and shapes for pile top attachments shall conform to ASTM A36 (AASHTO M183) or ASTM A 572 Grade 50 (AASHTO M183).

4.8	Centralizers

Centralizers shall be fabricated from plastic, steel, or material that is non-detrimental to the reinforcing steel.  Wood shall not be used.

4.9	Corrosion Protection 	Optional

The corrosion protection requirements, if any, are identified in Section 1.7.7 above. The Owner may therefore have no need to reproduce details in his Specification. This section may be deleted in its entirety if no corrosion protection materials will be required such as for compression piles in non-aggressive ground

4.9.1.  Epoxy Coating: If used, the thickness of coating applied electrostatically to the reinforcing steel shall be 7-12 mils.  Epoxy coating shall be in accordance with ASTM A775/AASHTO M282 or ASTM A936.  Bend test requirements shall be waived.  Bearing plates and nuts encased in the pile concrete footing may not be epoxy coated ( unless the footing reinforcement is epoxy coated).

4.9.2.  Galvanization :  If used, galvanization shall meet the requirements of ASTM A-153.

4.9.3.  Encapsulation : If used, the encapsulation shall meet the requirements of PTI “ Recommendations for Soil and Rock Anchors” (1996). These requirements are also presented in Appendix C.  The Specifier may use the above statement, reference and attach Appendix C or include Appendix C here

5.	EXECUTION

5.1	Installation

5.1.1	The micropile installation technique shall be such that it is consistent with the geotechnical, logistical, environmental, and load carrying conditions of the project.  The micropile contractor shall select the drilling method and the grouting procedures used for the installation of the micropiles, subject to the approval of the Owner.

5.1.2	The drilling equipment and methods shall be suitable for drilling through the conditions to be encountered, with minimal disturbance to these conditions or any overlying or adjacent structure or service.  The borehole must be open to the defined nominal diameter, full length, prior to placing grout and reinforcement.  This condition may exist in stable, competent materials without the need for temporary hole support.  Often however, some form of borehole wall support will be required for all or part of the pile length.  Such methods include temporary steel casing, hollow stem augers, or the use of a hole-stabilizing drilling fluid (provided it in no way has a deleterious effect on geotechnical bond development). Water and polymer slurry foams are typical micropile hole flushing media.  Air shall be used only with extreme caution, especially in the vicinity of existing structures or services.

5.1.3	All installation techniques shall be determined and scheduled such that there will be no interconnection or damage to piles in which grout has not achieved final set.

5.1.4	Centralizers shall be provided at 10-ft center maximum spacing on central reinforcement.  The uppermost centralizer shall be located a maximum of 5 ft from the top of the micropile.  Centralizers shall permit the free flow of grout without misalignment of the reinforcement.

5.1.5	The central reinforcement steel with centralizers shall be lowered into the stabilized drill holes to the desired depth without difficulty.  Partially inserted reinforcing bars shall not be driven or forced into the hole such that there will be no interconnection or damage to piles in which the grout has not achieved final set.

5.1.6	The grout shall be injected as per Section 5.2.2., below. (Steps 5.1.6 and 5.1.7 may be interchanged in response to site conditions.)

5.1.7	The Contractor shall check pile top elevations and adjust all installed micropiles to the planned elevations.

5.2	Grouting

5.2.1	The Contractor shall provide systems and equipment to measure the grout quality, quantity, and pumping pressure during the grouting operations.  This information is to be measured and recorded by the responsible party as identified in Table 1.

5.2.2	After drilling, the hole shall be flushed with water and/or air to remove drill cuttings and/or other loose debris.  The Contractor shall provide a stable, homogenous  neat cement grout or a sand cement grout with a minimum 28-day unconfined compressive strength of 4000 psi.  The grout shall not contain lumps or any other evidence of poor or incomplete mixing.  Admixtures, if used, shall be mixed in accordance with manufacturer’s recommendations.  The pump shall be equipped with a pressure gauge to monitor grout pressures.  The pressure gauge shall be capable of measuring pressures of at least 150 psi or twice the actual grout pressures used by the Contractor, whichever is greater.  The grouting equipment shall be sized to enable the grout to be pumped in one continuous operation.  The grout should be kept in constant agitation prior to pumping.

The grout shall be injected from the lowest point of the drill hole (by tremie methods) until clean, pure grout flows from the top of the micropile.  The tremie grout may be pumped through grout tubes, hollow stem augers, or drill rods.  Subsequent to tremie grouting, all grouting operations associated with , for example, extraction of drill casing and pressure grouting, must ensure complete continuity of the grout column. The use of compressed air to directly pressurize the fluid grout is not permissible.  The grout pressures and grout takes shall be controlled to prevent excessive heave in cohesive soils or fracturing of soil or rock formations.  The entire pile shall be grouted to the design cut-off level.

Upon completion of grouting of Type A and B piles, the grout tube may remain in the hole, but it shall be filled with grout.  For Type C and D piles, grout tubes shall be installed prior to the tremie grouting.

5.2.3	Grout within the micropiles shall be allowed to attain the minimum design strength prior to being loaded.

5.2.4	If the Contractor uses a post-grouting system, all relevant details including grouting pressure, volume, location and mix design, shall be submitted as part of Section 3.1.

5.3	Pile Splices

5.3.1	Pile splices shall be constructed to develop the required design strength of the pile section.

5.3.2	Lengths of casing and reinforcing steel to be spliced shall be secured in proper alignments and in such a manner that no eccentricity between the axes of the two lengths spliced or angle between them results.

6.	PILE LOAD TESTS

The total number of load tests, maximum test load capacities and load test schedules will vary on a project by project basis.  They are dependent on ground type, pile ultimate capacity and pile loadings type (i.e., static or seismic).  It is recommended to follow Post Tensioning Institute (PTI) guidelines for soil and rock anchors including creep test requirements in creep susceptible soils.

6.1	Pre-Production Pile Tests (Optional)

Pile load tests shall be performed to verify the adequacy of the design of the pile system, and the proposed construction procedures prior to installation of production piles.  ____ sacrificial test piles with dead weight, reaction piles, or ground anchors shall be constructed immediately prior to the commencement of the installation of the production micropiles.  The Owner shall determine the number of piles, their location, acceptable load and movement criteria, and the type(s) of loading direction.

The Contractor shall submit for review and acceptance the proposed micropile load testing procedure.  The testing program shall be provided 2 weeks prior to starting the load testing.  This micropile verification load testing proposal shall be in general conformance with ASTM D-1143 +/or D-3689, and shall indicate the minimum following information:

- Type and accuracy of apparatus for measuring load

- Type and accuracy of apparatus for applying load

- Type and accuracy of apparatus for measuring the pile deformation

- Type and capacity of reaction load system, including sealed design drawings

- Hydraulic jack calibration report

If the micropile load test fails to meet the design requirements, the cause(s) shall be established, and the Contractor shall modify the micropile design and/or installation methods and retest the new system, as directed by the Owner.  For Prescriptive Specifications, the Engineer will define the appropriate modifications.

These micropile load test results shall verify the suitability of the Contractor’s design and installation methods, and will be reviewed and accepted by the Owner prior to beginning production micropiles.  The tests shall be performed at a location to be determined by the Owner.

The drilling and grouting methods, casing and other reinforcement details, and depth of embedment for the test pile shall be identical to the production piles, except where approved otherwise by the Owner.

The tested micropiles shall be loaded to 200% of the compression and/or tension design load (DL)(i.e., 2.0 DL).  The load tested piles must be of the same design as the production piles to ensure meaningful results.  The jack shall be positioned at the beginning of the test such that the unloading and repositioning of the jack during the test will not be required.  Piles shall be tested under compression loads prior to testing under tension loads.  An Alignment Load (AL if required) shall be applied to the pile prior to setting the movement recording devices.  This Alignment Load shall be no more than 10% on Design Load (i.e., 0.1 DL): dial gauges shall be zeroed at the first setting of AL.

Axial pile load tests shall be made by loading the micropile and recording the pile head movement in the following load increments :

| LOAD | HOLD TIME (MINUTES) |
| --- | --- |
| AL | - |
| 0.15 DL | 2.5 |
| 0.30 DL | 2.5 |
| 0.45 DL | 2.5 |
| AL | 1 |
| 0.15 DL | 1 |
| 0.45 DL | 1 |
| 0.60 DL | 2.5 |
| 0.75 DL | 2.5 |
| 0.90 DL | 2.5 |
| 1.00 DL | 2.5 |
| AL | 1 |
| 0.15 DL | 1 |
| 1.00 DL | 1 |
| 1.15 DL | 2.5 |
| 1.30 DL | 10 * |
| 1.45 DL | 2.5 |
| AL | 1 |
| 0.15 DL | 1 |
| 1.45 DL | 1 |
| 1.60 DL | 1 |
| 1.75 DL | 2.5 |
| 1.90 DL | 2.5 |
| 2.00 DL | 10 |
| 1.50 DL | 5 |
| 1.00 DL | 5 |
| 0.50 DL | 5 |
| AL | 5 |

*	Hold until meet acceptance criterion 2 above

AL = Alignment Load; DL – Design Load

Thereafter for special test piles not to be later used in service, further load cycles may be conducted to failure.

It will be noted that this procedure is similar to the provisions of ASTM D-1143.

This cyclic loading method will permit all parties to conduct fundamental analyses of the performance since it allows elastic and permanent movements to be separated and studied separately.  However, a recent study suggests that the ultimate load carrying capacity of the pile may be reduced by repeated cyclic loading due to progressive debonding (Reference: “Observations of micropile performance under cyclic loading conditions” by Cavey et al. (2000).  Ground Improvement (4) pp 23-29).

Measurement of pile movement shall be obtained at each increment.  The load hold period shall start as soon as the test load is applied and the pile movement, with respect to a fixed reference, shall be measured and recorded at 1 minute, 2, 3, 4, and 5, and 10 minutes (load cycle maxima only).

The acceptance criteria for micropile verification load tests are:

1.	The pile shall sustain the compression and tension design capacities (1.0 DL) with no more than ____ in. total vertical movement at the top of the pile as measured relative to the top of the pile prior to the start of testing.  If an Alignment Load is used, then the allowable movement will be reduced by multiplying by a factor of (DL-AL)/DL.  (This conservatively accounts for the movement in reaching AL.

2.	Test piles shall have a creep rate at the end of the 130% DL increment which is not greater than 0.040 in./log cycle time from 1 to 10 minutes or 0.080 in./log cycle time from 6 to 60 minutes and has a linear or decreasing creep rate.

3.	Failure does not occur at the 2.0 DL maximum compression and tension loads.  Failure is defined as a slope of the load versus deflection (at end of increment) curve exceeding 0.025 inches/kip.  (This is a referenceable definition for piles used by NYSDOT and presented in the FHWA Static Pile Load Test Manual.)

The Contractor will provide the Owner a written report confirming micropile geometry and construction details within 7 working days after the completion of the pre-production tests.  This written confirmation will either confirm the bond lengths as shown in the drawings for micropiles or propose modifications based upon the results of the verification tests.

When a micropile fails to meet the acceptance criteria, modifications shall be made to the design, the construction procedures, or both.  These modifications include, but are not limited to, installing replacement micropiles, modifying the installation methods, increasing the bond length, regrouting via pre-placed re-grout tubes, or changing the micropile type.  Any modification which requires changes to the structure shall have prior review and acceptance of the Owner.  The cause for any modifications of design or construction procedures shall be decided in order to appropriately determine any additional cost implications.

6.2	Production Pile Testing (This may be the only type of load test conducted, depending on project conditions.)

The Contractor shall proof test at least a further ___ production micropiles.  The piles to be tested will be selected by the Owner. At the Contractor’s suggestion, but with the Owner’s concurrence, tension tests may be performed based to maximum DL in compression or tension for friction piles with sufficient structural tension capacity.

The test sequence shall be as follows:

| LOAD | HOLD TIME (MINUTES) |
| --- | --- |
| AL | - |
| 0.15 DL | 2.5 |
| 0.30 DL | 2.5 |
| 0.45 DL | 2.5 |
| 0.60 DL | 2.5 |
| 0.75 DL | 2.5 |
| 0.90 DL | 2.5 |
| 1.00 DL | 2.5 |
| 1.15 DL | 2.5 |
| 1.30 DL | 10* |
| 1.00 DL | 4 |
| 0.75 DL | 4 |
| 0.50 DL | 4 |
| 0.25 DL | 4 |
| AL | 4 |

AL = Alignment Load

DL = Design Load

* Hold until meet acceptance criterion 2 of next paragraph

The load increments of the above may be regarded as a minimum.  It is not unusual to test production piles to values of up to 2.0 DL.  This maximum test load is to be determined by the Owner.  For example, ASTM-D1143 stipulates testing to 2.0 DL.

The acceptance criteria for micropile proof load tests are:

1.	The pile shall sustain the compression and tension design capacities (1.0 DL) with no more than __ in. total vertical movement at the top of the pile as measured relative to the pile prior to the start of testing.  If an Alignment Load is used, then the allowable movement will be reduced by multiplying by a factor of (DL-AL)/DL.  (This conservatively accounts for the movement in reaching AL.)

2.	Test piles shall have a creep rate at the end of the 130% DL increment which is not  greater than 0.040 in./log cycle time from 1 to 10 minutes or 0.080 in./log cycle time from 6 to 60 minutes and has a linear or decreasing creep rate.

If a micropile that is proof tested fails to meet the acceptance criteria, the contractor shall be directed to proof test another micropile in the vicinity.  For failed piles and further construction of other piles, the Contractor shall modify the design, the construction procedure, or both.  These modifications include, but are not limited to, installing replacement micropiles, incorporating piles of reduced load capacities, modifying the installation methods, increasing the bond length, or changing the micropile type.  Any modification which requires changes to the structure shall have prior review and acceptance of the Owner.  Any modifications of design or construction procedures shall be at the Contractor’s expense.

6.3	Lateral Testing

If required, lateral loading testing shall be conducted – prior to axial testing – in accordance with ASTM 3966.  During both pre-production verification- and proof- test phases, care must be exercised to not cause permanent structural damage to the pile which will subsequently reduce its axial load capacity.  Therefore, the acceptance criterion, typically expressed as a maximum total movement at a certain load must be carefully selected by the Owner, as being realistic and not potentially damaging to the structure.

7.	MEASUREMENT AND PAYMENT

Micropile work can be paid for in different ways, reflecting the relative risk to be accepted by the Owner and the Contractor.  However, the following items are common and standard:

| QUANTITY | DESCRIPTION | UNIT |
| --- | --- | --- |
| 1 | Mobilization | Lump sum |
| 1 | Demobilization | Lump sum |
| 1 | Conduct pre-production test pile program of declared scope | Lump sum |
|  | Test Production Pile | Per pile |
| - | Obstructions | Per hour or Force Account |
|  | Pile Installation | As below |

The alternatives for paying for the production micropiles are:

- Per Unit Length:  Micropiles of the design capacity shall be paid for per lineal foot installed below initial ground surface elevation.

- Per Pile:  Micropiles of the design capacity shall be paid for on a “per pile” basis (no allowance for changes in length relative to that originally foreseen).

- Per Pile with Add/Deduct: Micropiles of the design capacity shall be paid for on a “per pile” basis, with a predetermined length, and an add/deduct figure per lineal foot to accommodate field changes.  This is typical for piles founded in rock.

- Lump Sum: The whole micropile system (exclusive of the common and standard elements above) shall be paid for on a “lump sum” basis.

Note:  In projects where it is difficult to estimate with confidence, grout takes (e.g., Karstic Limestone terrains), there should be an add/deduct item for grout volume also.

APPENDIX A

Guidance of Ground Agressiveness Classification

The most common and simplest tests utilized to measure the aggressiveness of the soil environment include electrical resistivity, pH, chloride, and sulfate.  Per FHWA-RD-89-198, the ground is considered aggressive if any one of these indicators show critical values as detailed below:

| Property | Test Designation | Critical Values |
| --- | --- | --- |
| Resistivity | AASHTO T–288 ASTM G 57 | below 2,000 ohm-cm |
| pH | AASHTO T–289 ASTM G 51 | below 5 |
| Sulfate | AASHTO T–290 ASTM 516M ASTM D4327 | above 200 ppm |
| Chloride | AASHTO T–291 ASTM 512 ASTM D4327 | above 100 ppm |

### APPENDIX B

Guidance on Sacrificial Steel Thickness

1.  AASTHO Standard Specifications for Highway Bridges, Section 4.5.7.4 Cross Section Adjustment for Corrosion states “ For concrete-filled pipe piles where corrosion may be expected, 1/16” inch shall be deducted from the shell thickness to allow for reduction in section due to corrosion.”

2.  CCTG (1992) Technical Rules for the Design and Calculation of the Foundations of Civil Engineering Works, Publication 62, Title V and FHWA-SA-97-070 present the following Table.

#### Minimum Dimensions (mm) of Sacrificial Shell Thickness as Corrosion Protection

| Soil Type | Service Life (years) |
| --- | --- |
|  | 25 | 50 | 75 | 100 |
| Not Aggressive | 0.25 | 0.60 | 0.70 | 0.80 |
| Barely Aggressive | 1.00 | 1.60 | 2.00 | 2.50 |
| Very Aggressive | 2.50 | 4.00 | 5.00 | 6.00 |

Converted to Imperial Units

#### Minimum Dimensions (in) of Sacrificial Shell Thickness as Corrosion Protection

| Soil Type | Service Life (years) |
| --- | --- |
|  | 25 | 50 | 75 | 100 |
| Not Aggressive | 0.010 | 0.025 | 0.027 | 0.031 |
| Barely Aggressive | 0.039 | 0.063 | 0.079 | 0.098 |
| Very Aggressive | 0.098 | 0.157 | 0.197 | 0.236 |

APPENDIX C

Details of corrosion protection requirements which may be incorporated into the Specifications by the Drafter if relevant.

Encapsulation Specification

C.1	Encapsulation and Related Topics: The annulus between the reinforcement and the encapsulating tube shall be a minimum of 0.2 in and be fully grouted with non-shrink grout conforming to Section 5.1.8 of these specifications.

C.1.1	Corrosion Inhibiting Compound: If required, the corrosion inhibiting compound placed in the free length shall be an organic compound (grease or wax) with appropriate polar moisture displacing, corrosion inhibiting additives and self-healing properties.  The compound shall permanently stay viscous and be chemically stable and nonreactive with the prestressing steel, the sheathing materials, and the anchor grout.

C.1.2	Bondbreaker: If required, the bondbreaker shall be fabricated from a smooth plastic tube or pipe having the following properties:

1.	Resistant to chemical attack from aggressive environment, grout, or corrosion inhibiting compound;

2.	Resistant to aging by ultra-violet light;

3.	Non-detrimental to the reinforcement; and

4.	Capable of withstanding abrasion, impact, and bending during handling and installation.

The bondbreaker allows the prestressing steel to elongate during testing and stressing.  Plastic tube or pipe made from medium to high density polyethylene conforming to ASTM D1248 (AASHTO M252) or from polyvinyl chloride conforming to ASTM D1784, Class 13464-B, or equivalent, with a minimum wall thickness of 0.04 in. have performed well.

C.1.3	Sheath: If required, the sheath shall be made of a material with the following properties:

1.	Resistant to chemical attack from aggressive environment, grout, or corrosion inhibiting compound;

2.	Resistant to aging by ultra-violet light;

3.	Non-detrimental to the reinforcement; and

4.	Capable of withstanding abrasion, impact, and bending during handling and installation.

5.	Enable the reinforcement to elongate during testing and stressing.

Tubing made from polyethylene or polypropylene shall have an average minimum wall thickness of 0.060 in., PVC tubing 0.040 in., and steel tubing or pipe 0.20 in.

The sheath is part of the corrosion protection system for the unbonded length.  A smooth sheath may also function as a bondbreaker.  Sheaths fabricated from one of the following have performed satisfactorily.

1.	A tube made from hot-melt extruded polyethylene conforming to ASTM D1248, Type III.

2.	A tube made from hot-melt extruded polypropylene conforming to PP 210 B55542-11, as defined by ASTM D4101.

3.	Steel tubing conforming to ASTM A500.

4.	Steel tubing conforming to ASTM A53.

5.	Pipe or tube of PVC conforming to ASTM D1784, Class 13464-B.

6.	A corrugated tube conforming to the requirement of the bond length encapsulation.

Sheaths fabricated from a corrugated tube or a heat shrinkable sleeve need the application of a separate bondbreaker.

C.1.4	Bond Length Encapsulations: If required, the bond length encapsulation shall be fabricated from material with the following properties:

1.	Capable of transferring stresses from the grout surrounding the reinforcement to the bond length grout:

2.	Able to accommodate movements during testing.

3.	Resistant to chemical attack from aggressive environment, grout, or corrosion inhibiting compound;

4.	Resistant to aging by ultra-violet light;

5.	Non-detrimental to the reinforcement; and

6.	Capable of withstanding abrasion, impact, and bending during handling and installation.

7.	Capable of resisting internal grouting pressures.

The encapsulation is part of the corrosion protection for the bond length.  Encapsulations fabricated from the following have performed satisfactorily:

1.	High density corrugated polyethylene tubing conforming to the requirements of AASHTO M252.1.

2.	Deformed steel tubing or pipes conforming to ASTM A53 or A500.

3.	Corrugated, polyvinyl chloride tubes manufactured from rigid PVC compounds conforming to ASTM D1784, Class 13464-B.

Tubing made from polyethylene or polypropylene shall have an average minimum wall thickness of 0.060 in., PVC tubing 0.040 in., and steel tubing or pipe 0.20 in.  HDPE tubing with a wall thickness of 0.04 in. can be used for pregrouted elements.

HDPE sheathing is sensitive to prolonged exposure of UV light and, when pregrouted, can be subject to stress cracking.

C.1.5	Heat Shrinkable Sleeves: If required, heat shrinkable sleeves shall be fabricated from a radiation cross-linked polyolefin tube internally coated with an adhesive sealant.  Heat shrinkable sleeves are mainly used for watertight connections or for sheaths on bar reinforcement.  Heat shrinkable sleeves with a nominal wall thickness of 24 mils and internally coated with an adhesive sealant with a nominal thickness of 20 mils have performed satisfactorily.